ROOF SPECIALTIES MECHANICAL & ELECTRICAL ROOF SUPPORTS Specification

Note: This mechanical and electrical roof support specification, with minor editing, has been written as a separate section of work. Alternatively, the appropriate clauses may be incorporated as part of a roofing specification. 

	PART 1 GENERAL

1.01	SECTION INCLUDES

A.	Supply and installation of roof accessories, including:
1.	Mechanical and electrical roof supports
2.   Preformed metal flashings

1.02	RELATED SECTIONS

A.	Section 03300 - Cast-in-Place Concrete

B.	Section 05210 - Steel Joists

C.	Section 05300 - Metal Deck

D.	Section 06100 - Rough Carpentry

E.	Section 07200 - Thermal Protection

F.	Section 07500 - Membrane Roofing

G.	Section 07900 - Joint Sealers

1.03	REFERENCES

A. The work of this Section to conform to:

Canadian

Note: CSA standard is applicable only to those Thaler products supplied with 
EPDM Triple Pressure Grommet Seal and/or EPDM Base Seal.

           1. CSA-B272-93-Prefabricated Self-Sealing Roof Vent Flashings
           
           2. CRCA (Canadian Roofing Contractor's Association). 
           
           3. SPRI (Single Ply Roofing Institute)
            
           4.  CUFCA (Canadian Urethane Foam Contractor's Association) and CGSB-51-GB-46MP, 
                Manual for "Installers of Spray Polyurethane Foam Thermal Insulation".
           
      5. CSA C40.21-M1987 and M350W (Structural Quality Steel). 

      6. CSA W47.1-1983 (Certification of Companies for Fusion Welding of Structural Steel)

            7. CSA W59-M1989 (Welded Steel Construction-Metal Arc Welding)

            8. CSA G164-M1981 (Hot dip Galvanizing of Irregularly Shaped Articles).

United States

          B. The work of this Section to conform to:

            1. NRCA (National Roofing Contractor's Association)
           
            2.  ASTM C1029-90 "Spray Applied Rigid Cellular Polyurethane Thermal Insulation".

            3.  AA 5AS-30 (Specifications for Aluminum Structures)

4. ASTM D3963/D M-87 (Structural Specification for Epoxy Coated Reinforced Steel).

5. ASTM A36 (Non Exposed Structural Components).

6. ASTM A123 (Standard Specification for Zinc Coating ( Hot Dip Galvanizing)  of  Iron and Steel Products.

7. ASTM Z325 (Bolts, Nuts and Washers) or Type 304 stainless steel.

8. AWS D1.1 (Structural Welding Code-Steel)

9. AWS D1.2 (Structural Welding Code-Aluminum)

  	    
1.04	SUBMITTALS

A.	Manufacturer's descriptive literature for each product, including section or other type details.

B.	Manufacturer's written installation instructions.

C.	Shop drawings and samples, when required, in accordance with Section [01300]. 

1.05	QUALITY ASSURANCE

A.	Roof accessories manufacturer's to have minimum 5 years documented experience in the design and fabrication of roofing specialties and accessories.

1.06	SPECIAL WARRANTY

A.	Warrant products installed under this section of work to be free of leaks, condensation and defects in materials and/or manufacture for a period of 20 years when installed in accordance with the manufacturer's written instructions.

	PART 2 PRODUCTS

2.01	MANUFACTURER

A.	 Provide products as manufactured by Thaler Metal Industries, 1-800-387-7217   (Mississauga, Ontario, Canada) or 1-800-576-1200 (Niagara Falls, NY) or provide equal products by another manufacturer approved in advance by the [Architect], based upon:
1.	20 year warranty against leaks, condensation and defects in materials and/or manufacture, as applicable;
2.	compliance with CSA B272-93 (Prefabricated Self-Sealing Roof Vent Flashings);
3.	air barrier flashing design using EPDM seals only. 
4.	maintenance free design;
5.	materials and sizes options, and thickness
6.	injection molded urethane insulation to CGSB-51-GP 46MP and ASTM C1029-90, as applicable;
7.	treated flashing deck flange, as applicable;
8.	written installation instructions.

2.02	MANUFACTURED UNITS

Note: Delete clauses not applicable.

       MERS-600A Aluminum Pipe Support (Single, Plain Pipe)
B.   Pipe supports (single plain pipe): Thaler MERS-600A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, and type 304 stainless steel pipe roller assembly sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-605A Aluminum Pipe Support (Double, Plain Pipe)
C.     Pipe supports (double plain pipe): Thaler MERS-605A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, and type 304 stainless steel pipe roller assemblies sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-610A Aluminum Pipe Support (Single, Insulated Pipe)
D.      Pipe supports (single insulated pipe): Thaler MERS-610A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, and type 304 stainless steel pipe cradle assembly sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-615A Aluminum Pipe Support (Double, Insulated Pipe)
E.       Pipe supports (double insulated pipe): Thaler MERS-615A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, and Type 304 stainless steel pipe cradle assemblies sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-620A Aluminum Re-Roofing Pipe Support (Single, Plain Pipe)
F.       Pipe supports (double insulated pipe): Thaler MERS-620A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, stirrup-type pipe holder, and Type 304 stainless steel pipe roller assembly sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-625A Aluminum Re-Roofing Pipe Support (Double, Plain Pipe)
G.      Pipe supports (double insulated pipe): Thaler MERS-625A adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, stirrup-type pipe holders, and Type 304 stainless steel pipe roller assemblies sized to suit [___] actual O.D. pipe: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.0321" (0.831 mm) 24 oz. copper] [.031" (0.79 mm 22 ga.) Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange][bituminous painted deck flange].
  
      MERS-630A-1 to 630A-8 Aluminum Pipe Support (Single, Double, Triple, Multiple, Large Insulated Pipe)
H.      Pipe supports (single, double, triple or multiple, large insulated pipe): Thaler MERS-630A-1 to MERS-630A-8 adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, cross-bar carrier with EPDM end caps, and Type 304 stainless steel pipe cradle assemblies sized to suit [___] actual O.D. pipes: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

   MERS-650A-1 to 650A-8 Re-Roofing Aluminum Pipe Supports (Single, Double, Triple, Multiple, Insulated Pipe)
I.     Pipe supports (single, double, triple or multiple, insulated pipe): Thaler MERS-650A-1 to MERS-650A-8 adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck, cross-bar carrier, and Type 304 stainless steel pipe cradle assemblies sized to suit [___] actual O.D. pipes: [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

     MERS-700   Terrace Lighting Roof Support 
J.       Terrace lighting roof supports: Thaler MERS-700, [14" (356 mm) high] [18" (457 mm) high] epoxy coated, urethane insulated hollow structural steel including appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck; galvanized threaded cap with [___] dia. s.s. lighting pole adapter stub; weatherproof 5/8" (16 mm) lock bolt with EPDM seal to prevent counter-rotation of support and lighting pole (by others); manufacturer's standard urethane insulated [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], flashing with EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].
  
      MERS-707-1/-2/-3/-4/ Gas Line/Conduit Roof Supports (All Metal) 
K.    Gas line/conduit roof supports: Thaler [MERS-707-1] [MERS-70702] [MERS-707-3] [MERS-707-4] supports for [___ dia. pipe size(s)] [pipe sizes as shown on the drawings]; with; 6061-T6 alloy, mill finish, extruded aluminum base assembly and Type 304 stainless steel roller and clearance type retaining strap, all sized to suit pipe diameter(s) [and EPDM end caps].

      MERS-708 Tiered Gas Line/Conduit Roof Supports 
L.    Tiered gas line/conduit roof supports: Thaler MERS-708 supports, tiered as indicated: with: 6061-T6 alloy mill finish, extruded aluminum cross-bar carrier assemblies, Type 304 stainless steel roller and clearance type retaining straps, all sized to suit pipe diameters [and EPDM end caps]; adjustable height 6061-T6 hollow aluminum, mill finish, urethane insulated vertical base supports, 2' (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and matching, fixed ( non-adjustable) intermediate vertical supports;  [SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New Standard STACK JACK flashing for steel deck], 7" (178 mm) high, consisting of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.031" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].
           
      MERS-709 Combo Pipe & Cross-Over Stair
M.   Combination pipe supports and cross-over stair: Thaler MERS-709 Combo Pipe Supports and Cross-Over Stair, consisting of [single] [double] [triple] [quadruple] pipe supports with; 6061-T6 alloy mill finish, extruded aluminum base assembly and Type 304 stainless steel roller and clearance type retaning straps, all sized to suit pipe diameter(s) [and EPDM end caps]; 6061-T6 mill finish aluminum cross-over stair (Thaler ARS-680 Stair) of size shown on the drawings with 3-3/4" x 3-3/4" x 1/4" (95 mm x 95 mm x 6 mm) aluminum stringer/platform support beams, 1/8" x 1-1/2" x 9" x 3'-0" (3 mm x 38 mm x 229 mm 915 mm) alum. threads [screwed] [welded] to 1-1/2"  x 1-1/2" x 1/2' (38 mm x 38 mm x 12 mm) alum. stringer angle supports and platform support beams, 1-1/2" (38 mm) dia. Schedule 40 pipe rail; adjustable height hollow aluminum, urethane insulated pipe and stair supports urethane insulated vertical base supports, 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and [SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New Standard STACK JACK flashing for steel deck], 7" (178 mm) high, consisting of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

      MERS-730 Security Lighting Roof Support
N.    Security lighting roof supports: Thaler MERS-730 epoxy coated, urethane insulated hollow steel support including appropriate mounting hardware (adhesive type supplied by others) for fastening to structural roof deck (galvanized optional) threaded steel cap with 2" (51 mm) dia. conduit head: weather proof 3/4" (19 mm) lock-bolts with EPDM seals to prevent counter-rotation of cap/conduit head; and manufacturer's standard urethane insulated  [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel] flashing with EPDM Base Seal [PVC coated deck flange] [bituminous painted deck flange].

        MERS-740 Miscellaneous Lighting Roof Support
O.       Security lighting roof supports: Thaler MERS-740 adjustable height, epoxy coated, urethane insulated hollow structural steel supports including appropriate mounting hardware (adhesive type supplied by others) for fastening to structural roof deck, cap/plate assembly with three s.s. studs located to suit light fixture (by others), set screw to lock cap in place; and manufacturer's standard urethane insulated  [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel] flashing with EPDM Base Seal [PVC coated deck flange] [bituminous painted deck flange].
    
        MERS-800A  Duct Support 
P.       Duct supports: Thaler MERS-800A, adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and cross-bar carrier assembly of length to suit application  with EPDM end caps; [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].
 
        MERS-850A   Re-Roofing Duct Support 
Q.      Re-roofing duct supports: Thaler MERS-850A, 16" to 23" (405 mm to 584 mm) high adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and cross-bar carrier assembly of length to suit application; [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.032" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].
  
         MERS-900A  Air Handling Unit Support (Small Units)
R.       Air handling unit supports: Thaler MERS-900A, 16" to 28" (406 mm to 711 mm) high adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and cross-bar carrier of length to suit application with EPDM end caps, anti-vibration pads and 1-1/2" (38 mm) dia. pipe section reinforcing ties; [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.0321" (0.831 mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].
   
        MERS-915A and MERS-925A  Air Handling Unit Support (Medium Units) 
             
              Note: For specification clauses, change MERS-900A model number to MERS-915A or MERS-925A model number as desired.      
        
        MERS-920A Air Handling Unit Support (Large Units) 
            
            Note: For specification clauses, change MERS-900A model number to MERS-920A.      

          MERS-910A   Re-Roofing Air Handling Unit Support (Small Units) 
S.       Re-roofing air handling unit supports: Thaler MERS-910A, 16" to 23" (406 mm to 584 mm) high adjustable height 6061-T6 hollow aluminum with mill finish, urethane insulated supports 2" (51 mm) dia., with appropriate hardware (adhesive type supplied by others) for fastening to structural roof deck and cross-bar carrier of length to suit application with EPDM  anti-vibration pads, and 1-1/2" (38 mm) dia. pipe section reinforcing ties; [ SJ-34 non-insulated New-Standard STACK JACK flashing for concrete deck] [SJ-37 pre-insulated New-Standard STACK JACK flashing for steel deck] 7" (178 mm) high, consisting  of [.064" (1.6 mm) mill finish 1100-0T alloy aluminum] [.0321" (0.831mm) 24 oz. copper] [.031" (0.79 mm) 22 ga. Type 304 stainless steel], 2" (51 mm) dia., to CSA B272-93, with EPDM Triple Pressure Grommet Seal and EPDM Base Seal and [PVC coated deck flange] [bituminous painted deck flange].

        MERS-930A and MERS-935A Re-Roofing Air Handling Unit Support (Medium Units) 
         
         Note: For specification clauses, change MERS-910A model number to MERS-930A or MERS-935A model number as desired.     
        
         MERS-940A Re-Roofing Air Handling Unit Support (Large Units) 
          
Note: For specification clauses, change MERS-910A model number to MERS-940A. 

PART 3 EXECUTION

3.01	EXAMINATION 

A.	Report to the Contractor in writing, defects of work prepared by other trades and other unsatisfactory site conditions. Verify site dimensions. Commencement of work will imply acceptance of prepared work.

            3.02	PREPARATION

Note: The following clauses apply to retrofit installations only.

A.	For retrofit work, remove existing roof assembly as necessary to allow for installation of supports.

B.	In the event of structural deficiencies, deck corrosion or deterioration, ensure that a structural engineer has assessed and approved all surfaces upon which the work of this Section depends. Institute repairs and/or reinforcement where necessary.

C.	If necessary, protect building interior and contents against ingression of water, dust, debris or other material.

3.03	INSTALLATION

Note: Delete clauses not applicable.

A.	Roof Supports

1.	Install anchors or equipment in accordance with manufacturer’s printed instructions, shop drawings and as specified.

2.	Ensure supports are installed under the direct supervision of a Professional Engineer [and Roofing Consultant].

3.	Where necessary, provide protection against deterioration due to contact of dissimilar materials.

4.	Ensure work is inspected prior to application of roofing.

B.	Flashing

1.	Install roof support flashing in accordance with manufacturer’s printed instructions.

BUR
2.    Set flashing deck flange in layer of plastic cement and flash in with 3 overlapping layers of felt flashing.

Modified Bitumen
3.   Torch membrane until bitumen is fluid and set flashing deck flange into fluid. Flash in flange with two overlapping layers of ModBit and seal with asphalt sealer. Do not overheat (melt) EPDM Base Seal.

Single Ply
4.    Set deck flange in layer of membrane adhesive and extend single ply up sleeve to highest elevation possible and clamp membrane to STACK JACK Flashing.

Note: For PVC membrane, specify PVC coated flashing; weld roofing to deck flange using PVC torch.

PVC Single Ply
5.    Set deck flange in layer of membrane adhesive and extend single ply up sleeve to highest elevation possible and clamp membrane to flashing. Weld roofing to deck flange using PVC torch.

3.04	FIELD QUALITY CONTROL

A.	Comply with the requirements of Section [01400 - Quality Control].

3.05	ADJUSTING 

A.	Verify that all manufactured units have been installed in accordance with specifications and details, and will function as intended. Adjust any items where necessary to ensure proper operation.

3.06	CLEANING

A.	Clean manufactured units using materials and methods approved by manufacturer. Do not use cleaners or techniques which could impair performance of the roofing system.

End of Section